G.P. DRAIN SURVEYS

CLEANING, JETTING, RE-LINING, REPAIRS & SURVEYS

__________________________________________________________________________________________________________________________________________________________________________________________________________

REGISTERED OFFICE:									       THORNY CROFT

56 B SCATCHERD LANE

MORLEY

LEEDS

LS27 OJJ

TEL\FAX:   0113 2533154

MOBILE:     07973 834690

Our Ref : GMP/lhg/2977

Your Ref : Paul Watchorn

29th November 2022

Adept Consulting Engineers

1912 Mill

Sunny Bank Mills

Farlsey

Leeds

For the attention of : Paul Watchorn.

DRAINAGE SURVEY REPORT.

Site at Rose Garden Café Sheffield.

### Manhole	Invert		Pipe Size	Material	Service

1		350mm		4”		Plastic		Combined

2		480mm		4”		Clay		Combined

3		610mm		4”		Clay		Combined

4		1220mm		4” & 6”		Clay		Combined

M/H1 – B1

- – Start scan

- to 04.9 – Silt within the drain

04.9 – End of survey – unable to continue – appears to be out of use

Conclusion

No action required.

M/H1 – B2

- – Start scan

03.0 – Blind branch 2.0’clock

05.6 – Blind branch 9.0’clock

06.5 – Blind branch 2.0’clock

07.9 – Blind branch 9.0’clock

08.3 – Blind branch 2.0’clock

10.7 – End survey at a rest bend

Conclusion

This drainage run serves all of the WC’s for all of the toilet blocks, no further action required.

M/H1 – B3

- – Start scan

- to 04.4 – Silt within the drain

04.4 – End survey at a RWP

Conclusion

We recommend that this drainage run be high-pressure water jet/vac cleaned.

2

M/H4 – B4

- – Start scan

03.8 – End survey at M/H2

Conclusion

No action required.

M/H2 – B1

- – Start scan

02.2 – Minor radial crack

02.7 – End survey at M/H3

Conclusion

The radial crack is such a minor fault we would recommend no further action.

M/H3 – B1

- – Start scan

00.4 – Radial crack

01.1 – Radial crack

03.1 – Mass of rubble – drain out of use

Conclusion

No action required.

M/H3 – B2

- – Start scan

00.2 – Radial crack

02.2 – Mass of rubble – drain out of use

Conclusion

No action required.

M/H3 – B3

- – Start scan

00.3 – Radial crack

00.7 – Radial crack

01.2 – Radial crack

04.7 – End survey at a RW Gully

Conclusion

We recommend that the three radial cracks be structurally patch-line repaired.

M/H3 – B4

- – Start scan

00.3 – Radial crack

00.8 – Radial crack

02.2 – Drain capped off – drain out of use

Conclusion

No action required.

M/H3 – B5

- – Start scan

05.0 – Blind branch 11.0’clock

07.4 – Minor root intrusions

07.4 – Blind branch 11.0’clock

13.1 – Blind branch 11.0’clock

18.0 – Minor radial crack

18.3 – Drain increases in size from 4” to 6”

19.4 – End survey at M/H4

Conclusion

The minor root intrusions and minor radial crack are such minor faults we would recommend no further action.

3

M/H4 – B1

- – Start scan

04.7 – Mass of rubble – drain out of use

Conclusion

No action required.

M/H4 – B2

- – Start scan

05.5 – Mass of rubble – drain out of use

Conclusion

No action required.

M/H4 – B3

- – Start scan

- to 05.7 – Silt within the drain

05.7 – End survey at an out of use concealed Gully

Conclusion

No action required.

M/H4 – B4

- – Start scan

00.0 to 25.4 – Silt within the drain

00.3 – Radial crack

15.8 – Line of the drain deviates left

25.2 – Blind branch 9.0’clock

25.4 – Unable to continue survey due to the bend restricting pushing the push rod camera

Conclusion

We recommend that this drainage run be high-pressure water jet/vac cleaned and the radial crack structurally patch-line repaired.

M/H4 – B5

- – Start scan

00.1 – Minor root intrusions

00.8 – Multiple fractures

02.2 – Mass of rubble – drain out of use

Conclusion

No action required.

M/H4 – B6

- – Start scan

00.5 – Windsor trap

04.4 – Minor root intrusions

12.0 – Root intrusions & radial crack

13.3 – Radial fracture

13.9 – End survey at another Manhole

Conclusion

We recommend that the root intrusions & radial crack at 12.0 metres and the radial fracture at 13.3 metres be structurally patch-line repaired.

4

COMMENTS ON OUR FINDINGS.

We were instructed to attend site to carry out a full C.C.T.V. Drainage survey of the existing drainage serving the café. We have already recommended repairs within the report and all of this work should be carried out.

We were informed that the café has experienced blockages in the past and we have to assume that this was more than likely the waste pipes from the kitchens waste and gullies. It could be that simple servicing of the waste traps from the sinks needs to be carried out once the kitchen is back up and running.

Our price to carry out all of the high-pressure jet/vac cleaning and structural patch-line repairs would be  :   £4320.00 plus VAT.

Please see drawing for reference.

END OF SURVEY.